## Sheet1
THIS IS BASED ON 24 VOLT DEVICES ONLY | [8 empty] | Point to Point Method |  |  | End of Line Method
Project Name | [5 empty] | Calculations and allowable |  |  | CIRCUIT IS WITHIN LIMITS |  |  | CIRCUIT IS WITHIN LIMITS
Date | [5 empty] | voltage drop are based on
Circuit Number | [5 empty] | revised UL 1971 & 464 standards |  |  | Totals |  | Voltage | Totals |  | Voltage
Area Covered | [5 empty] | for current and limits. |  |  | Current | Distance | Drop | Current | Distance | Drop
Nominal System Voltage |  |  | 20.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum Device Voltage |  |  | 16 | [6 empty] | End of Line Voltage | 20.4 |  | End of Line Voltage | 20.4
Total Circuit Current |  | 0 |  | Wire | Ohm's |  |  |  |  | Percent Drop | 0% |  | Percent Drop | 0%
|  |  |  | Gauge | Per 1000 | End of Line method uses only the wire guage for the first device to source for calculation
Distance from source to 1st device |  |  |  | 18 | 7.07 | Standard Wire Resistance in Ohms per 1000 feet @ 27 C.
Wire Gauge for balance of circuit |  |  |  | 10 | 1.21 |  |  | 18=7.77 | 16=4.89 | 14=3.07 | 12=1.93 | 10=1.21
Enter current in amps. |  | Distance |  |  |  |  | 18-14 Awg = Solid Conductors 12-10 Awg = Stranded Conductors
.150 = 150 ma |  | from | Voltage |  |  | This circuit is sourced from:
Device | Device | previous | At | Drop from | Percent
Number | Current | device | Device | source | Drop
Device 1 |  | 0 | 20.4 | 0 | 0% | Notes:
END |  |  | 20.4 | 0 | 0% | Wire resistance is doubled in the calculations for two wires (Positive and Negative)
END |  |  | 20.4 | 0 | 0% | The voltage calculated to the last device in any method must not be lower then
END |  |  | 20.4 | 0 | 0% | the manufactures listed minimum operating voltage (IE: rated operating voltage16-33 VDC).
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0% | Device Manufacturer |  |  |  |  | Device Manufacturer
END |  |  | 20.4 | 0 | 0% |  |  |  | Current @Rated Voltage |  |  |  |  | Current @Rated Voltage
END |  |  | 20.4 | 0 | 0% | Horn Strobes |  |  |  |  | Strobe Only
END |  |  | 20.4 | 0 | 0% | Model # |  | Candela |  |  | Model # |  | Candela
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
END |  |  | 20.4 | 0 | 0%
Totals |  | 0 | End of Line Voltage |  | 20.4