## Instructions
Step
1 | List all of the items included in the fire alarm system which will rely on *this* battery-set for secondary power.
1A | Using the manufacturer's provided data sheets, indicate the standby or quiessent current requirement for each device in the fire alarm system.
1B | Using the manufacturer's provided data sheets, indicate the alarm current requirement for each device in the fire alarm system.
2
2A | Use NFPA 72-2002 4.4.1.5.3.1 to determine the standby time requirement, in hours, for this particular fire alarm system based upon its type.
2B | Use NFPA 72-2002 4.4.1.5.3.1 to determine the alarm time requirement, in hours, for this particular fire alarm system based upon its type.
3
3A | Add the standby and alarm battery-set sizes together.
3B | Add an optional factor of safety (20% or more) to determine the final battery-set size.
NOTES | a. Convert electrical current units into amps. 1000ma = 1A
b. Convert time units into hours. 5 minutes = .083 hour
c. To add a 20% safety factor, multiply the required battery-set size by 1.2 (120%).
NOTICE | The materials herein are provided as is and without any express or implied warranty of any kind including warranties of merchantability, noninfringement of intellectual property, or fitness for any particular purpose. In no event shall Automatic Fire Alarm Association (AFAA) be liable for any damages whatsoever (including, without limitation, damages for loss of profits, business interruption, loss of information) arising out of the use of or inability to use the materials, even if AFAA has been advised of the possibility of such damages. Because some jurisdictions prohibit the exclusion or limitation of liability for consequential or incidental damages, the above limitation may not apply to you. AFAA further does not warrant the accuracy or completeness of the information, text, graphics, links or other items contained within these materials. AFAA may make changes to these materials, or to the products described therein, at any time without notice. AFAA makes no commitment to update the Materials.

## Data Entry
| STEP 1A | [6 empty] | STEP 1B
| ITEM | DESCRIPTION | STANDBY CURRENT PER UNIT (AMPS) |  | QTY |  | TOTAL STANDBY CURRENT PER ITEM | ALARM CURRENT PER UNIT |  | QTY |  | TOTAL ALARM CURRENT PER ITEM
STEP 1 | FACU | Fire Alarm Control Unit | 0.1 | X | 1 | = |  | 0.2 | X | 1 | =
| SD | Smoke Detector | 0.001 | X | 30 | = |  | 0.05 | X | 15 | =
| HD | Heat Detector (mech) | 0 | X | 5 | = |  | 0 | X | 0 | =
| RLY | Relay (failsafe) | 0.05 | X | 0 | = |  | 0 | X | 3 | =
| RLY | Relay (not failsafe) | 0 | X | 4 | = |  | 0.05 | X | 3 | =
| HS | Horn-Strobe | 0 | X | 18 | = |  | 0.075 | X | 10 | =
| DH | Door Holder | 0.065 | X | 4 | = |  | 0 | X | 0 | =
| ANN | Annunciator | 0.1 | X | 1 | = |  | 0.2 | X | 1 | =
| MS | Manual Station | 0 | X | 8 | = |  | 0 | X | 5 | =
| WF | Waterflow Switch | 0 | X | 6 | = |  | 0 | X | 4 | =
| TS | Tamper Switch | 0 | X | 6 | = |  | 0 | X | 4 | =
|  |  |  | X |  | = |  |  | X |  | =
|  |  |  | X |  | = |  |  | X |  | =
| TOTAL SYSTEM | [6 empty] | TOTAL SYSTEM
| STANDBY CURRENT (AMPS) | [6 empty] | ALARM CURRENT (AMPS)
|  |  | STEP 2A |  |  |  |  | STEP 2B
STEP 2 | Prepared for: |  | REQUIRED STANDBY TIME (HRS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM STANDBY CURRENT (AMPS) |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) | REQUIRED ALARM TIME (HOURS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM ALARM CURRENT (AMPS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS)
|  |  | 24 | X |  | = |  | 0.083 | X |  | =
|  |  | STEP 3A |  |  |  |  | STEP 3B
STEP 3 | Prepared by: |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS) |  | TOTAL CAPACITY (AMP-HOURS) | TOTAL CAPACITY (AMP-HOURS) |  | SAFETY FACTOR (OPTIONAL) |  | ADJUSTED BATTERY CAPACITY (AMP-HOURS)
|  |  |  | + |  | = |  |  | X | 20% | =

## Obscured
ITEM | DESCRIPTION | STANDBY CURRENT PER UNIT (AMPS) |  | QTY |  | TOTAL STANDBY CURRENT PER ITEM | ALARM CURRENT PER UNIT (AMPS) |  | QTY |  | TOTAL ALARM CURRENT PER ITEM
FACU | Fire Alarm Control Unit | 0.1 | X | 1 | = |  | 0.2 | X | 1 | =
SD | Smoke Detector | 0.001 | X | 20 | = |  | 0.05 | X | 20 | =
RLY | Heat Detector | 0 | X | 6 | = |  | 0 | X | 6 | =
RLY | Relay (failsafe) | 0.05 | X | 0 | = |  | 0 | X | 1 | =
HS | Relay (not failsafe) | 0 | X | 15 | = |  | 0.05 | X | 15 | =
DH | Horn-Strobe | 0 | X | 18 | = |  | 0.075 | X | 10 | =
ANN | Door Holder | 0.065 | X | 4 | = |  | 0 | X | 0 | =
#REF! | Annunciator | 0.1 | X | 1 | = |  | 0.2 | X | 1 | =
MS | Manual Station | 0 | X | 8 | = |  | 0 | X | 5 | =
WF | Waterflow Switch | 0 | X | 6 | = |  | 0 | X | 4 | =
TS | Tamper Switch | 0 | X | 6 | = |  | 0 | X | 4 | =
0 | 0 | 0 | X | 0 | = |  | 0 | X | 0 | =
0 | 0 | 0 | X | 0 | = |  | 0 | X | 0 | =
TOTAL SYSTEM STANDBY CURRENT (AMPS) | [6 empty] | TOTAL SYSTEM ALARM CURRENT (AMPS)
Prepared By: |  | REQUIRED STANDBY TIME (HRS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM STANDBY CURRENT (AMPS) |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) | REQUIRED ALARM TIME (HOURS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM ALARM CURRENT (AMPS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS)
|  | 24 | X |  | = |  | 0.083 | X |  | =
Prepared by: |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS) |  | TOTAL CAPACITY (AMP-HOURS) | TOTAL CAPACITY (AMP-HOURS) |  | SAFETY FACTOR (%) |  | ADJUSTED BATTERY CAPACITY (AMP-HOURS)
|  |  | + |  | = |  |  | + | 20% | =

## Completed
ITEM | DESCRIPTION | STANDBY CURRENT PER UNIT (AMPS) |  | QTY |  | TOTAL STANDBY CURRENT PER ITEM | ALARM CURRENT PER UNIT (AMPS) |  | QTY |  | TOTAL ALARM CURRENT PER ITEM
FACU | Fire Alarm Control Unit | 0.1 | X | 1 | = | 0.1 | 0.2 | X | 1 | = | 0.2
SD | Smoke Detector | 0.001 | X | 20 | = | 0.02 | 0.05 | X | 20 | = | 1
HD | Heat Detector | 0 | X | 6 | = | 0 | 0 | X | 6 | = | 0
RLY | Relay (failsafe) | 0.05 | X | 0 | = | 0 | 0 | X | 1 | = | 0
RLY | Relay (not failsafe) | 0 | X | 15 | = | 0 | 0.05 | X | 15 | = | 0.75
HS | Horn-Strobe | 0 | X | 18 | = | 0 | 0.075 | X | 10 | = | 0.75
DH | Door Holder | 0.065 | X | 4 | = | 0.26 | 0 | X | 0 | = | 0
ANN | Annunciator | 0.1 | X | 1 | = | 0.1 | 0.2 | X | 1 | = | 0.2
MS | Manual Station | 0 | X | 8 | = | 0 | 0 | X | 5 | = | 0
WF | Waterflow Switch | 0 | X | 6 | = | 0 | 0 | X | 4 | = | 0
TS | Tamper Switch | 0 | X | 6 | = | 0 | 0 | X | 4 | = | 0
0 | 0 | 0 | X | 0 | = | 0 | 0 | X | 0 | = | 0
0 | 0 | 0 | X | 0 | = | 0 | 0 | X | 0 | = | 0
TOTAL SYSTEM STANDBY CURRENT (AMPS) | [5 empty] | 0.48 | TOTAL SYSTEM ALARM CURRENT (AMPS) |  |  |  | 2.9
Prepared for: |  | REQUIRED STANDBY TIME (HRS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM STANDBY CURRENT (AMPS) |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) | REQUIRED ALARM TIME (HOURS) NFPA 72-2002 4.4.1.5.3.1 |  | TOTAL SYSTEM ALARM CURRENT (AMPS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS)
|  | 24 | X | 0.48 | = | 11.52 | 0.083 | X | 2.9 | = | 0.2407
Prepared by: |  | REQUIRED STANDBY CAPACITY (AMP-HOURS) |  | REQUIRED ALARM CAPACITY (AMP-HOURS) |  | TOTAL CAPACITY (AMP-HOURS) | TOTAL CAPACITY (AMP-HOURS) |  | SAFETY FACTOR |  | ADJUSTED BATTERY CAPACITY (AMP-HOURS)
|  | 11.52 | + | 0.2407 | = | 11.7607 | 11.7607 | X | 120% | = | 14.1128