## Sheet1
THIS IS BASED ON 24 VOLT DEVICES ONLY | [8 empty] | Point to Point Method |  |  | End of Line Method
Project Name | [5 empty] | Calculations and allowable |  |  | CIRCUIT IS WITHIN LIMITS |  |  | CIRCUIT IS WITHIN LIMITS
Date | [5 empty] | voltage drop are based on
Circuit Number | [5 empty] | revised UL 1971 & 464 standards |  |  | Totals |  | Voltage | Totals |  | Voltage
Area Covered | [5 empty] | for current and limits. |  |  | Current | Distance | Drop | Current | Distance | Drop
Nominal System Voltage |  |  | 20.4 | [5 empty] | 1.582 | 415 | 2.327 | 1.582 | 415 | 4.1887
Minimum Device Voltage |  |  | 16 | [6 empty] | End of Line Voltage | 18.073 |  | End of Line Voltage | 16.2113
Total Circuit Current |  | 1.582 |  | Wire | Ohm's |  |  |  |  | Percent Drop | 11.41% |  | Percent Drop | 20.53%
|  |  |  | Gauge | Per 1000 | End of Line method uses only the wire guage for the first device to source for calculation
Distance from source to 1st device |  |  | 20 | 14 | 3.19 | Wire Resistance in Ohms per 1000 feet @ 75°C.
Wire Gauge for balance of circuit |  |  |  | 14 | 3.19 |  |  | 18=8.08 | 16=5.08 | 14=3.19 | 12=2.01 | 10=1.26
Enter current in amps. |  | Distance |  |  |  |  | 18-10 Awg = Solid Conductors |  |  | NEC - Chapter 9, Table 8
.150 = 150 ma |  | from | Voltage |  |  | This circuit is sourced from:
Device | Device | previous | At | Drop from | Percent
Number | Current | device | Device | source | Drop
Device 1 | 0.125 | 20 | 20.1981 | 0.20186 | 0.9895% | Notes:
Device 2 | 0.125 | 20 | 20.0122 | 0.38778 | 1.901% | Wire resistance is doubled in the calculations for two wires (Positive and Negative)
Device 3 | 0.166 | 50 | 19.5873 | 0.81268 | 3.984% | The voltage calculated to the last device in any method must not be lower then
Device 4 | 0.25 | 50 | 19.2154 | 1.1846 | 5.807% | the manufactures listed minimum operating voltage (IE: rated operating voltage16-33 VDC).
Device 5 | 0.125 | 75 | 18.7771 | 1.6229 | 7.956%
Device 6 | 0.125 | 50 | 18.5247 | 1.8753 | 9.193% | Device Manufacturer |  |  |  |  | Device Manufacturer
Device 7 | 0.166 | 50 | 18.3123 | 2.0877 | 10.23% |  |  |  | Current @Rated Voltage |  |  |  |  | Current @Rated Voltage
Device 8 | 0.25 | 50 | 18.1528 | 2.2472 | 11.02% | Horn Strobes |  |  |  |  | Strobe Only
Device 9 | 0.25 | 50 | 18.073 | 2.327 | 11.41% | Model # |  | Candela |  |  | Model # |  | Candela
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
END |  |  | 18.073 | 2.327 | 11.41%
Totals |  | 415 | End of Line Voltage |  | 18.073