## Sheet1
THIS IS BASED ON 24 VOLT DEVICES ONLY | [8 empty] | Point to Point Method |  |  | End of Line Method
Project Name |  | Sample Fire Alarm Project |  |  |  | Calculations and allowable |  |  | CIRCUIT IS WITHIN LIMITS |  |  | CIRCUIT IS WITHIN LIMITS
Date | [5 empty] | voltage drop are based on
Circuit Number | [5 empty] | revised UL 1971 & 464 standards |  |  | Totals |  | Voltage | Totals |  | Voltage
Area Covered | [5 empty] | for current and limits. |  |  | Current | Distance | Drop | Current | Distance | Drop
Nominal System Voltage |  |  | 20.4 | [5 empty] | 1.582 | 415 | 2.2394 | 1.582 | 415 | 4.0311
Minimum Device Voltage |  |  | 16 | [6 empty] | End of Line Voltage | 18.1606 |  | End of Line Voltage | 16.3689
Total Circuit Current |  | 1.582 |  | Wire | Ohm's |  |  |  |  | Percent Drop | 10.98% |  | Percent Drop | 19.76%
|  |  |  | Gauge | Per 1000 | End of Line method uses only the wire guage for the first device to source for calculation
Distance from source to 1st device |  |  | 20 | 14 | 3.07 | Wire Resistance in Ohms per 1000 feet @ 75°C.
Wire Gauge for balance of circuit |  |  |  | 14 | 3.07 |  |  | 18=7.77 | 16=4.89 | 14=3.07 | 12=1.93 | 10=1.21
Enter current in amps. |  | Distance |  |  |  |  | 18-10 Awg = Solid Conductors |  |  | NEC - Chapter 9, Table 8
.150 = 150 ma |  | from | Voltage |  |  | This circuit is sourced from:
Device | Device | previous | At | Drop from | Percent
Number | Current | device | Device | source | Drop
Device 1 | 0.125 | 20 | 20.2057 | 0.19427 | 0.9523% | Notes:
Device 2 | 0.125 | 20 | 20.0268 | 0.37319 | 1.829% | Wire resistance is doubled in the calculations for two wires (Positive and Negative)
Device 3 | 0.166 | 50 | 19.6179 | 0.78211 | 3.834% | The voltage calculated to the last device in any method must not be lower then
Device 4 | 0.25 | 50 | 19.2599 | 1.1401 | 5.589% | the manufactures listed minimum operating voltage (IE: rated operating voltage16-33 VDC).
Device 5 | 0.125 | 75 | 18.8381 | 1.5619 | 7.656%
Device 6 | 0.125 | 50 | 18.5953 | 1.8047 | 8.847% | Device Manufacturer |  |  |  |  | Device Manufacturer
Device 7 | 0.166 | 50 | 18.3908 | 2.0092 | 9.849% |  |  |  | Current @Rated Voltage |  |  |  |  | Current @Rated Voltage
Device 8 | 0.25 | 50 | 18.2373 | 2.1627 | 10.6% | Horn Strobes |  |  |  |  | Strobe Only
Device 9 | 0.25 | 50 | 18.1606 | 2.2394 | 10.98% | Model # |  | Candela |  |  | Model # |  | Candela
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
END |  |  | 18.1606 | 2.2394 | 10.98%
Totals |  | 415 | End of Line Voltage |  | 18.1606